## Buses
Bus | Graph_Loc_x | Graph_Loc_y
src_node | 4 | 12
n0 | 4 | 11
n1 | 0 | 5
n2 | 0 | 4
n3 | 0 | 3
n4 | 0 | 2
n5 | 1 | 7
n6 | 1 | 6
n7 | 1 | 5
n8 | 1 | 4
n9 | 2 | 9
n10 | 2 | 6
n11 | 2 | 5
n12 | 2 | 4
n13 | 2 | 3
n14 | 3 | 10
n15 | 3 | 9
n16 | 3 | 8
n17 | 3 | 7
n18 | 3 | 6
n19 | 3 | 4
n20 | 4 | 4
n21 | 3 | 2
n22 | 3 | 1
n23 | 3 | 0
n24 | 4 | 10
n25 | 4 | 9
n26 | 4 | 3
n27 | 4 | 2
n28 | 4 | 8
n29 | 5 | 10
n30 | 5 | 9
n31 | 5 | 8
n32 | 5 | 7
n33 | 5 | 6
n34 | 5 | 5
n35 | 6 | 9
n36 | 6 | 8
n37 | 6 | 7
n38 | 6 | 6
n39 | 5 | 4
n40 | 5 | 2
n41 | 5 | 1
n42 | 6 | 4
n43 | 6 | 3
n44 | 3 | -1

## LineGeometry
LineGeo | Type | phase_cond | neutral_cond | Nphases | Nconds | 1_x | 1_z | 2_x | 2_z | 3_x | 3_z | 4_x | 4_z | Units | cond_pos
OH3p | OH | 2/0__ACSR | 1/0__ACSR | 3 | 4 | -5 | 28 | 0 | 28 | 5 | 28 | 0.5 | 24 | ft | abc
OH2p | OH | 1/0__ACSR |  | 2 | 2 | -5 | 28 | 5 | 28 |  |  |  |  | ft | ac
OH1p | OH | 1/0__ACSR | 1/0__ACSR | 1 | 2 | 0 | 28 | 0.5 | 24 |  |  |  |  | ft | b
UG3p | CN | 3/0_CLASS A_AA | 1/3_3/0(19×) | 3 | 3 | -0.41667 | -4 | 0 | -4 | 0.41667 | -4 |  |  | ft | abc
UG1p | CN | 2/0_CLASS A_AA | 1/3_2/0(19×) | 1 | 1 | 0 | -4 | [6 empty] | ft | b
OH3pD | OH | 2/0__ACSR |  | 3 | 3 | -5 | 28 | 0 | 28 | 5 | 28 |  |  | ft | abc

## Lines
bus1 | bus2 | Length | LineGeometry | Units | phases | cond_pos
n0 | n14 | 3 | OH3p | mi | 3
n14 | n15 | 3 | OH3p | mi | 3
n15 | n16 | 3 | OH3p | mi | 3
n16 | n17 | 3 | OH3p | mi | 3
n17 | n18 | 3 | OH3p | mi | 3
n18 | n19 | 3 | OH3p | mi | 3
n19 | n20 | 3 | OH1p | mi | 1
n19 | n21 | 3 | OH3p | mi | 3
n21 | n22 | 3 | OH3p | mi | 3
n22 | n23 | 3 | OH3p | mi | 3
n5 | n6 | 100 | OH2p | ft | 2
n6 | n7 | 100 | OH2p | ft | 2
n7 | n8 | 100 | OH2p | ft | 2
n7 | n1 | 100 | OH2p | ft | 2
n1 | n2 | 100 | OH2p | ft | 2
n2 | n3 | 100 | OH2p | ft | 2
n3 | n4 | 100 | OH2p | ft | 2
n6 | n10 | 100 | OH2p | ft | 2
n10 | n11 | 100 | OH2p | ft | 2
n11 | n12 | 100 | OH2p | ft | 2
n12 | n13 | 100 | OH2p | ft | 2
n20 | n26 | 3 | OH1p | mi | 1
n26 | n27 | 3 | OH1p | mi | 1
n39 | n40 | 100 | OH1p | ft | 1
n40 | n41 | 100 | OH1p | ft | 1
n39 | n42 | 100 | OH1p | ft | 1
n42 | n43 | 100 | OH1p | ft | 1
n0 | n29 | 3 | UG3p | mi | 3
n29 | n30 | 3 | UG3p | mi | 3
n30 | n31 | 3 | UG3p | mi | 3
n31 | n32 | 3 | UG3p | mi | 3
n32 | n33 | 3 | UG3p | mi | 3
n33 | n34 | 3 | UG3p | mi | 3
n30 | n35 | 3 | UG1p | mi | 1
n35 | n36 | 3 | UG1p | mi | 1
n36 | n37 | 3 | UG1p | mi | 1
n37 | n38 | 3 | UG1p | mi | 1
n24 | n25 | 100 | OH3pD | ft | 3

## Regulators
bus | kVA | phases | vbase | vreg | band | CTprim | Ctsec
src_node | 5000 | 3 | 120 | 126 | 2 | 600 | 5
n16 | 5000 | 3 | 120 | 124 | 2 | 600 | 5
n18 | 5000 | 3 | 120 | 124 | 2 | 600 | 5

## Transformers
bus1 | bus2 | xfmr | kV1 | kV2 | kVA1 | kVA2 | conn1 | conn2 | phases | windings | R | X | nll | wnd1_terms | wnd2_terms | wnd3_terms
src_node | n0 | 3p_120_12.47_2000_dw | 120 | 12.47 | 2000 | 2000 | delta | wye | 3 | 2 | 0.358 | 5.636 | 0.1 | 1.2.3 | 1.2.3
n14 | n24 | 3p_12.47_0.416_150_wd | 12.47 | 0.416 | 150 | 150 | wye | delta | 3 | 2 | 1 | 1.9 | 0.18 | 1.2.3 | 1.2.3
n15 | n9 | 3p_12.47_0.416_150_wd | 12.47 | 0.416 | 150 | 150 | wye | delta | 3 | 2 | 1 | 1.9 | 0.18 | 1.2.3 | 1.2.3
n17 | n5 | 2p_12.47_0.416_75_dd | 12.47 | 0.416 | 75 | 75 | delta | delta | 2 | 2 | 1 | 2 | 0.18 | 1.3 | 1.3
n31 | n28 | 3p_12.47_0.416_150_wd | 12.47 | 0.416 | 150 | 150 | wye | delta | 3 | 2 | 1 | 1.9 | 0.18 | 1.2.3 | 1.2.3
n20 | n39 | 1p_7.2_0.24_50_ww | 7.2 | 0.24 | 50 | 50 | wye | wye | 1 | 2 | 1.2 | 2 | 0.2 | 2 | 2
n23 | n44 | 3p_12.47_0.416_300_wd | 12.47 | 0.416 | 300 | 300 | wye | delta | 3 | 2 | 0.7 | 3.21 | 0.12 | 1.2.3 | 1.2.3

## Transformer Info
kV_hv | kV_lv | kVA_hv | kVA_lv | Conn_hv | Conn_lv | Phases | Windings | R | X | nll | name
120 | 12.47 | 2000 | 2000 | delta | wye | 3 | 2 | 0.358 | 5.636 | 0.1 | 3p_120_12.47_2000_dw
12.47 | 0.416 | 500 | 500 | wye | delta | 3 | 2 | 0.9 | 4.75 | 0.1 | 3p_12.47_0.416_500_wd
12.47 | 0.416 | 300 | 300 | wye | delta | 3 | 2 | 0.7 | 3.21 | 0.12 | 3p_12.47_0.416_300_wd
12.47 | 0.416 | 150 | 150 | wye | delta | 3 | 2 | 1 | 1.9 | 0.18 | 3p_12.47_0.416_150_wd
7.2 | 0.24 | 100 | 100 | wye | wye | 1 | 2 | 0.8 | 2.2 | 0.2 | 1p_7.2_0.24_100_ww
7.2 | 0.24 | 75 | 75 | wye | wye | 1 | 2 | 1 | 2 | 0.2 | 1p_7.2_0.24_75_ww
12.47 | 0.416 | 75 | 75 | delta | delta | 2 | 2 | 1 | 2 | 0.18 | 2p_12.47_0.416_75_dd
7.2 | 0.24 | 50 | 50 | wye | wye | 1 | 2 | 1.2 | 2 | 0.2 | 1p_7.2_0.24_50_ww
7.2 | 0.24 | 25 | 25 | wye | wye | 1 | 2 | 1.6 | 2.5 | 0.2 | 1p_7.2_0.24_25_ww

## Loads
Bus | Phases | kW | kVAr | CondPos | kV
n2 | 2 | 7 | 2 | 1.3 | 0.24
n3 | 2 | 6 | 2 | 1.3 | 0.24
n4 | 2 | 15 | 4.5 | 1.3 | 0.24
n8 | 2 | 10 | 4 | 1.3 | 0.24
n9 | 3 | 50 | 20 | 1.2.3 | 0.416
n11 | 2 | 2 | 0.5 | 1.3 | 0.24
n12 | 2 | 3 | 1 | 1.3 | 0.24
n13 | 2 | 10 | 4 | 1.3 | 0.24
n16 | 3 | 70 | 10 | 1.2.3 | 12.47
n18 | 3 | 30 | 13 | 1.2.3 | 12.47
n21 | 3 | 60 | 20 | 1.2.3 | 12.47
n25 | 3 | 60 | 15 | 1.2.3 | 0.416
n26 | 1 | 130 | 35 | 2 | 7.2
n27 | 1 | 90 | 33 | 2 | 7.2
n28 | 3 | 115 | 60 | 1.2.3 | 0.416
n29 | 3 | 66 | 23 | 1.2.3 | 12.47
n32 | 3 | 70 | 20 | 1.2.3 | 12.47
n33 | 3 | 25 | 10 | 1.2.3 | 12.47
n34 | 3 | 35 | 12 | 1.2.3 | 12.47
n36 | 1 | 30 | 16 | 2 | 7.2
n37 | 1 | 95 | 25 | 2 | 7.2
n38 | 1 | 40 | 16 | 2 | 7.2
n40 | 1 | 7 | 2 | 2 | 0.24
n41 | 1 | 6 | 3 | 2 | 0.24
n42 | 1 | 7 | 2 | 2 | 0.24
n43 | 1 | 14 | 7 | 2 | 0.24
n44 | 3 | 140 | 70 | 1.2.3 | 0.416

## circuit
slack_bus | basekv | pu | phases | R_1 | X_1 | R_0 | X_0
src_node | 120 | 1.033 | 3 | 0.3 | 0.3 | 0.7 | 0.7

## Ref
OH | mi | abc | delta.delta | delta.wye | wye.delta | wye.wye | delta | 1 | Line
CN | kft | ab | 0 | -30 | -30 | 0 | wye | 2 | Transformer
TS | km | ac | -60 | -150 | -150 | 180 |  | 3
| mi | bc | -120 | 150 | 150 |  |  | 1.2
| ft | a | -180 | 30 | 30 |  |  | 1.3
| in | b | 120 |  |  |  |  | 2.3
| cm | c | 60 |  |  |  |  | 2.1
3.1
3.2
1.2.3
2.3.1
3.1.2
1.3.2
3.2.1
2.1.3

## WireData
Type | Size | Stranding | Material | Diam | GMRac | rac | normamps | GMRunits | runits | Size_Material
1__ACSR | 1 |  | ACSR | 0.355 | 0.00418 | 1.38 | 200 | ft | mi | 1_ACSR
1_7 STRD_Copper | 1 | 7 STRD | Copper | 0.328 | 0.00992 | 0.765 | 270 | ft | mi | 1_Copper
1_CLASS A_AA | 1 | CLASS A | AA | 0.328 | 0.00991 | 1.224 | 177 | ft | mi | 1_AA
2_6/1_ACSR | 2 | 6/1 | ACSR | 0.316 | 0.00418 | 1.69 | 180 | ft | mi | 2_ACSR
2_7 STRD_Copper | 2 | 7 STRD | Copper | 0.292 | 0.00883 | 0.964 | 230 | ft | mi | 2_Copper
2_7/1_ACSR | 2 | 7/1 | ACSR | 0.325 | 0.00504 | 1.65 | 180 | ft | mi | 2_ACSR
2_AWG SLD_Copper | 2 | AWG SLD | Copper | 0.258 | 0.00836 | 0.945 | 220 | ft | mi | 2_Copper
2_CLASS A_AA | 2 | CLASS A | AA | 0.292 | 0.00883 | 1.541 | 156 | ft | mi | 2_AA
3_6/1_ACSR | 3 | 6/1 | ACSR | 0.281 | 0.0043 | 2.07 | 160 | ft | mi | 3_ACSR
3_AWG SLD_Copper | 3 | AWG SLD | Copper | 0.229 | 0.00745 | 1.192 | 190 | ft | mi | 3_Copper
4_6/1_ACSR | 4 | 6/1 | ACSR | 0.25 | 0.00437 | 2.57 | 140 | ft | mi | 4_ACSR
4_7/1_ACSR | 4 | 7/1 | ACSR | 0.257 | 0.00452 | 2.55 | 140 | ft | mi | 4_ACSR
4_AWG SLD_Copper | 4 | AWG SLD | Copper | 0.204 | 0.00663 | 1.503 | 170 | ft | mi | 4_Copper
4_CLASS A_AA | 4 | CLASS A | AA | 0.232 | 0.007 | 2.453 | 90 | ft | mi | 4_AA
5_6/1_ACSR | 5 | 6/1 | ACSR | 0.223 | 0.00416 | 3.18 | 120 | ft | mi | 5_ACSR
5_AWG SLD_Copper | 5 | AWG SLD | Copper | 0.1819 | 0.0059 | 1.895 | 140 | ft | mi | 5_Copper
6_6/1_ACSR | 6 | 6/1 | ACSR | 0.198 | 0.00394 | 3.98 | 100 | ft | mi | 6_ACSR
6_AWG SLD_Copper | 6 | AWG SLD | Copper | 0.162 | 0.00526 | 2.39 | 120 | ft | mi | 6_Copper
6_CLASS A_AA | 6 | CLASS A | AA | 0.184 | 0.00555 | 3.903 | 65 | ft | mi | 6_AA
7_AWG SLD_Copper | 7 | AWG SLD | Copper | 0.1443 | 0.00468 | 3.01 | 110 | ft | mi | 7_Copper
8_AWG SLD_Copper | 8 | AWG SLD | Copper | 0.1285 | 0.00416 | 3.8 | 90 | ft | mi | 8_Copper
9_AWG SLD_Copper | 9 | AWG SLD | Copper | 0.1144 | 0.00371 | 4.6758 | 80 | ft | mi | 9_Copper
10_AWG SLD_Copper | 10 | AWG SLD | Copper | 0.1019 | 0.0033 | 5.9026 | 75 | ft | mi | 10_Copper
12_AWG SLD_Copper | 12 | AWG SLD | Copper | 0.0808 | 0.00262 | 9.3747 | 40 | ft | mi | 12_Copper
14_AWG SLD_Copper | 14 | AWG SLD | Copper | 0.0641 | 0.00208 | 14.8722 | 20 | ft | mi | 14_Copper
16_AWG SLD_Copper | 16 | AWG SLD | Copper | 0.0508 | 0.00164 | 23.7262 | 10 | ft | mi | 16_Copper
18_AWG SLD_Copper | 18 | AWG SLD | Copper | 0.0403 | 0.0013 | 37.6726 | 5 | ft | mi | 18_Copper
19_AWG SLD_Copper | 19 | AWG SLD | Copper | 0.0359 | 0.00116 | 47.5103 | 4 | ft | mi | 19_Copper
20_AWG SLD_Copper | 20 | AWG SLD | Copper | 0.032 | 0.00103 | 59.684 | 3 | ft | mi | 20_Copper
22_AWG SLD_Copper | 22 | AWG SLD | Copper | 0.0253 | 0.00082 | 95.4835 | 2 | ft | mi | 22_Copper
24_AWG SLD_Copper | 24 | AWG SLD | Copper | 0.0201 | 0.00065 | 151.616 | 1 | ft | mi | 24_Copper
1/0__ACSR | 1/0 |  | ACSR | 0.398 | 0.00446 | 1.12 | 230 | ft | mi | 1/0_ACSR
1/0_7 STRD_Copper | 1/0 | 7 STRD | Copper | 0.368 | 0.01113 | 0.607 | 310 | ft | mi | 1/0_Copper
1/0_CLASS A_AA | 1/0 | CLASS A | AA | 0.368 | 0.0111 | 0.97 | 202 | ft | mi | 1/0_AA
2/0__ACSR | 2/0 |  | ACSR | 0.447 | 0.0051 | 0.895 | 270 | ft | mi | 2/0_ACSR
2/0_7 STRD_Copper | 2/0 | 7 STRD | Copper | 0.414 | 0.01252 | 0.481 | 360 | ft | mi | 2/0_Copper
2/0_CLASS A_AA | 2/0 | CLASS A | AA | 0.414 | 0.0125 | 0.769 | 230 | ft | mi | 2/0_AA
3/0_12 STRD_Copper | 3/0 | 12 STRD | Copper | 0.492 | 0.01559 | 0.382 | 420 | ft | mi | 3/0_Copper
3/0_6/1_ACSR | 3/0 | 6/1 | ACSR | 0.502 | 0.006 | 0.723 | 300 | ft | mi | 3/0_ACSR
3/0_7 STRD_Copper | 3/0 | 7 STRD | Copper | 0.464 | 0.01404 | 0.382 | 420 | ft | mi | 3/0_Copper
3/0_CLASS A_AA | 3/0 | CLASS A | AA | 0.464 | 0.014 | 0.611 | 263 | ft | mi | 3/0_AA
3/8_INCH STE_Steel | 3/8 | INCH STE | Steel | 0.375 | 1e-05 | 4.3 | 150 | ft | mi | 3/8_Steel
4/0_12 STRD_Copper | 4/0 | 12 STRD | Copper | 0.552 | 0.0175 | 0.303 | 490 | ft | mi | 4/0_Copper
4/0_19 STRD_Copper | 4/0 | 19 STRD | Copper | 0.528 | 0.01668 | 0.303 | 480 | ft | mi | 4/0_Copper
4/0_6/1_ACSR | 4/0 | 6/1 | ACSR | 0.563 | 0.00814 | 0.592 | 340 | ft | mi | 4/0_ACSR
4/0_7 STRD_Copper | 4/0 | 7 STRD | Copper | 0.522 | 0.01579 | 0.303 | 480 | ft | mi | 4/0_Copper
4/0_CLASS A_AA | 4/0 | CLASS A | AA | 0.522 | 0.0158 | 0.484 | 299 | ft | mi | 4/0_AA
250_12 STRD_Copper | 250 | 12 STRD | Copper | 0.6 | 0.01902 | 0.257 | 540 | ft | mi | 250_Copper
250_19 STRD_Copper | 250 | 19 STRD | Copper | 0.574 | 0.01813 | 0.257 | 540 | ft | mi | 250_Copper
250_CON LAY_AA | 250 | CON LAY | AA | 0.567 | 0.0171 | 0.41 | 329 | ft | mi | 250_AA
266.8_26/7_ACSR | 266.8 | 26/7 | ACSR | 0.642 | 0.0217 | 0.385 | 460 | ft | mi | 266.8_ACSR
266.8_CLASS A_AA | 266.8 | CLASS A | AA | 0.586 | 0.0177 | 0.384 | 320 | ft | mi | 266.8_AA
300_12 STRD_Copper | 300 | 12 STRD | Copper | 0.657 | 0.0208 | 0.215 | 610 | ft | mi | 300_Copper
300_19 STRD_Copper | 300 | 19 STRD | Copper | 0.629 | 0.01987 | 0.215 | 610 | ft | mi | 300_Copper
300_26/7_ACSR | 300 | 26/7 | ACSR | 0.68 | 0.023 | 0.342 | 490 | ft | mi | 300_ACSR
300_30/7_ACSR | 300 | 30/7 | ACSR | 0.7 | 0.0241 | 0.342 | 500 | ft | mi | 300_ACSR
300_CON LAY_AA | 300 | CON LAY | AA | 0.629 | 0.0198 | 0.342 | 350 | ft | mi | 300_AA
336.4_26/7_ACSR | 336.4 | 26/7 | ACSR | 0.721 | 0.0244 | 0.306 | 530 | ft | mi | 336.4_ACSR
336.4_30/7_ACSR | 336.4 | 30/7 | ACSR | 0.741 | 0.0255 | 0.306 | 530 | ft | mi | 336.4_ACSR
336.4_CLASS A_AA | 336.4 | CLASS A | AA | 0.666 | 0.021 | 0.305 | 410 | ft | mi | 336.4_AA
350_12 STRD_Copper | 350 | 12 STRD | Copper | 0.71 | 0.0225 | 0.1845 | 670 | ft | mi | 350_Copper
350_19 STRD_Copper | 350 | 19 STRD | Copper | 0.679 | 0.0214 | 0.1845 | 670 | ft | mi | 350_Copper
350_CON LAY_AA | 350 | CON LAY | AA | 0.679 | 0.0214 | 0.294 | 399 | ft | mi | 350_AA
397.5_26/7_ACSR | 397.5 | 26/7 | ACSR | 0.783 | 0.0265 | 0.259 | 590 | ft | mi | 397.5_ACSR
397.5_30/7_ACSR | 397.5 | 30/7 | ACSR | 0.806 | 0.0278 | 0.259 | 600 | ft | mi | 397.5_ACSR
397.5_CLASS A_AA | 397.5 | CLASS A | AA | 0.724 | 0.0228 | 0.258 | 440 | ft | mi | 397.5_AA
400_19 STRD_Copper | 400 | 19 STRD | Copper | 0.726 | 0.0229 | 0.1619 | 730 | ft | mi | 400_Copper
450_19 STRD_Copper | 450 | 19 STRD | Copper | 0.77 | 0.0243 | 0.1443 | 780 | ft | mi | 450_Copper
450_CON LAG_AA | 450 | CON LAG | AA | 0.77 | 0.0243 | 0.229 | 450 | ft | mi | 450_AA
477_26/7_ACSR | 477 | 26/7 | ACSR | 0.858 | 0.029 | 0.216 | 670 | ft | mi | 477_ACSR
477_30/7_ACSR | 477 | 30/7 | ACSR | 0.883 | 0.0304 | 0.216 | 670 | ft | mi | 477_ACSR
477_CLASS A_AA | 477 | CLASS A | AA | 0.795 | 0.0254 | 0.216 | 510 | ft | mi | 477_AA
500_19 STRD_Copper | 500 | 19 STRD | Copper | 0.811 | 0.0256 | 0.1303 | 840 | ft | mi | 500_Copper
500_37 STRD_Copper | 500 | 37 STRD | Copper | 0.814 | 0.026 | 0.1303 | 840 | ft | mi | 500_Copper
500_CON LAY_AA | 500 | CON LAY | AA | 0.813 | 0.026 | 0.206 | 483 | ft | mi | 500_AA
556.5_26/7_ACSR | 556.5 | 26/7 | ACSR | 0.927 | 0.0313 | 0.1859 | 730 | ft | mi | 556.5_ACSR
556.5_30/7_ACSR | 556.5 | 30/7 | ACSR | 0.953 | 0.0328 | 0.1859 | 730 | ft | mi | 556.5_ACSR
556.5_CLASS A_AA | 556.5 | CLASS A | AA | 0.858 | 0.0275 | 0.186 | 560 | ft | mi | 556.5_AA
600_37 STRD_Copper | 600 | 37 STRD | Copper | 0.891 | 0.0285 | 0.1095 | 940 | ft | mi | 600_Copper
600_CON LAY_AA | 600 | CON LAY | AA | 0.891 | 0.0285 | 0.172 | 520 | ft | mi | 600_AA
605_26/7_ACSR | 605 | 26/7 | ACSR | 0.966 | 0.0327 | 0.172 | 760 | ft | mi | 605_ACSR
605_54/7_ACSR | 605 | 54/7 | ACSR | 0.953 | 0.0321 | 0.1775 | 750 | ft | mi | 605_ACSR
636_27/7_ACSR | 636 | 27/7 | ACSR | 0.99 | 0.0335 | 0.1618 | 780 | ft | mi | 636_ACSR
636_30/19_ACSR | 636 | 30/19 | ACSR | 1.019 | 0.0351 | 0.1618 | 780 | ft | mi | 636_ACSR
636_54/7_ACSR | 636 | 54/7 | ACSR | 0.977 | 0.0329 | 0.1688 | 770 | ft | mi | 636_ACSR
636_CLASS A_AA | 636 | CLASS A | AA | 0.918 | 0.0294 | 0.163 | 620 | ft | mi | 636_AA
666.6_54/7_ACSR | 666.6 | 54/7 | ACSR | 1 | 0.0337 | 0.1601 | 800 | ft | mi | 666.6_ACSR
700_37 STRD_Copper | 700 | 37 STRD | Copper | 0.963 | 0.0308 | 0.0947 | 1040 | ft | mi | 700_Copper
700_CON LAY_AA | 700 | CON LAY | AA | 0.963 | 0.0308 | 0.148 | 580 | ft | mi | 700_AA
715.5_26/7_ACSR | 715.5 | 26/7 | ACSR | 1.051 | 0.0355 | 0.1442 | 840 | ft | mi | 715.5_ACSR
715.5_30/19_ACSR | 715.5 | 30/19 | ACSR | 1.081 | 0.0372 | 0.1442 | 840 | ft | mi | 715.5_ACSR
715.5_54/7_ACSR | 715.5 | 54/7 | ACSR | 1.036 | 0.0349 | 0.1482 | 830 | ft | mi | 715.5_ACSR
715.5_CLASS A_AA | 715.5 | CLASS A | AA | 0.974 | 0.0312 | 0.145 | 680 | ft | mi | 715.5_AA
750_37 STRD_AA | 750 | 37 STRD | AA | 0.997 | 0.0319 | 0.0888 | 1090 | ft | mi | 750_AA
750_CON LAY_AA | 750 | CON LAY | AA | 0.997 | 0.0319 | 0.139 | 602 | ft | mi | 750_AA
795_26/7_ACSR | 795 | 26/7 | ACSR | 1.108 | 0.0375 | 0.1288 | 900 | ft | mi | 795_ACSR
795_30/19_ACSR | 795 | 30/19 | ACSR | 1.14 | 0.0393 | 0.1288 | 910 | ft | mi | 795_ACSR
795_54/7_ACSR | 795 | 54/7 | ACSR | 1.093 | 0.0368 | 0.1378 | 900 | ft | mi | 795_ACSR
795_CLASS A_AA | 795 | CLASS A | AA | 1.026 | 0.0328 | 0.131 | 720 | ft | mi | 795_AA

## CNData
Type | Neutral Ampacity | Conductor Size | Phase Conductor Name | DiaIns | Diameter Over Screen (in) | DiaCable | Copper Neutral | Ampacity in Underground Duct (A) | Voltage Rating (kV) | Neutral Strand AWG | Rstrand | k | GMRac | GmrStrand | GMRunits | Rac | Runits | diam | normamps | DiaStrand | Radunits
Full_2(7×) | Full | 2(7×) | 2_CLASS A_AA | 0.78 | 0.85 | 0.98 | 10 × 14 | 120 | 15 | 14 | 14.8722 | 10 | 0.00883 | 0.00208 | ft | 1.541 | mi | 0.292 | 156 | 0.0641 | in
Full_1(19×) | Full | 1(19×) | 1_CLASS A_AA | 0.81 | 0.89 | 1.02 | 13 × 14 | 135 | 15 | 14 | 14.8722 | 13 | 0.00991 | 0.00208 | ft | 1.224 | mi | 0.328 | 177 | 0.0641 | in
Full_1/0(19×) | Full | 1/0(19×) | 1/0_CLASS A_AA | 0.85 | 0.93 | 1.06 | 16 × 14 | 155 | 15 | 14 | 14.8722 | 16 | 0.0111 | 0.00208 | ft | 0.97 | mi | 0.368 | 202 | 0.0641 | in
Full_2/0(19×) | Full | 2/0(19×) | 2/0_CLASS A_AA | 0.9 | 0.97 | 1.13 | 13 × 12 | 175 | 15 | 12 | 9.3747 | 13 | 0.0125 | 0.00262 | ft | 0.769 | mi | 0.414 | 230 | 0.0808 | in
Full_3/0(19×) | Full | 3/0(19×) | 3/0_CLASS A_AA | 0.95 | 1.02 | 1.18 | 16 × 12 | 200 | 15 | 12 | 9.3747 | 16 | 0.014 | 0.00262 | ft | 0.611 | mi | 0.464 | 263 | 0.0808 | in
Full_4/0(19×) | Full | 4/0(19×) | 4/0_CLASS A_AA | 1.01 | 1.08 | 1.28 | 13 × 10 | 230 | 15 | 10 | 5.9026 | 13 | 0.0158 | 0.0033 | ft | 0.484 | mi | 0.522 | 299 | 0.1019 | in
Full_250(37×) | Full | 250(37×) | 250_CON LAY_AA | 1.06 | 1.16 | 1.37 | 16 × 10 | 255 | 15 | 10 | 5.9026 | 16 | 0.0171 | 0.0033 | ft | 0.41 | mi | 0.567 | 329 | 0.1019 | in
Full_350(37×) | Full | 350(37×) | 350_CON LAY_AA | 1.17 | 1.27 | 1.47 | 20 × 10 | 300 | 15 | 10 | 5.9026 | 20 | 0.0214 | 0.0033 | ft | 0.294 | mi | 0.679 | 399 | 0.1019 | in
1/3_2(7×) | 1/3 | 2(7×) | 2_CLASS A_AA | 0.78 | 0.85 | 0.98 | 6 × 14 | 135 | 15 | 14 | 14.8722 | 6 | 0.00883 | 0.00208 | ft | 1.541 | mi | 0.292 | 156 | 0.0641 | in
1/3_1(19×) | 1/3 | 1(19×) | 1_CLASS A_AA | 0.81 | 0.89 | 1.02 | 6 × 14 | 155 | 15 | 14 | 14.8722 | 6 | 0.00991 | 0.00208 | ft | 1.224 | mi | 0.328 | 177 | 0.0641 | in
1/3_1/0(19×) | 1/3 | 1/0(19×) | 1/0_CLASS A_AA | 0.85 | 0.93 | 1.06 | 6 × 14 | 175 | 15 | 14 | 14.8722 | 6 | 0.0111 | 0.00208 | ft | 0.97 | mi | 0.368 | 202 | 0.0641 | in
1/3_2/0(19×) | 1/3 | 2/0(19×) | 2/0_CLASS A_AA | 0.9 | 0.97 | 1.1 | 7 × 14 | 200 | 15 | 14 | 14.8722 | 7 | 0.0125 | 0.00208 | ft | 0.769 | mi | 0.414 | 230 | 0.0641 | in
1/3_3/0(19×) | 1/3 | 3/0(19×) | 3/0_CLASS A_AA | 0.95 | 1.02 | 1.15 | 9 × 14 | 230 | 15 | 14 | 14.8722 | 9 | 0.014 | 0.00208 | ft | 0.611 | mi | 0.464 | 263 | 0.0641 | in
1/3_4/0(19×) | 1/3 | 4/0(19×) | 4/0_CLASS A_AA | 1.01 | 1.08 | 1.21 | 11 × 14 | 240 | 15 | 14 | 14.8722 | 11 | 0.0158 | 0.00208 | ft | 0.484 | mi | 0.522 | 299 | 0.0641 | in
1/3_250(37×) | 1/3 | 250(37×) | 250_CON LAY_AA | 1.06 | 1.16 | 1.29 | 13 × 14 | 260 | 15 | 14 | 14.8722 | 13 | 0.0171 | 0.00208 | ft | 0.41 | mi | 0.567 | 329 | 0.0641 | in
1/3_350(37×) | 1/3 | 350(37×) | 350_CON LAY_AA | 1.17 | 1.27 | 1.39 | 18 × 14 | 320 | 15 | 14 | 14.8722 | 18 | 0.0214 | 0.00208 | ft | 0.294 | mi | 0.679 | 399 | 0.0641 | in
1/3_500(37×) | 1/3 | 500(37×) | 500_CON LAY_AA | 1.29 | 1.39 | 1.56 | 16 × 12 | 385 | 15 | 12 | 9.3747 | 16 | 0.026 | 0.00262 | ft | 0.206 | mi | 0.813 | 483 | 0.0808 | in
1/3_750(61×) | 1/3 | 750(61×) | 750_37 STRD_AA | 1.49 | 1.59 | 1.79 | 15 × 10 | 470 | 15 | 10 | 5.9026 | 15 | 0.0319 | 0.0033 | ft | 0.0888 | mi | 0.997 | 1090 | 0.1019 | in

## TSData
Type | Diameter Over Insulation (in) | Diameter Over Screen (in) | Jacket Thickness (mils) | Outside Diameter | Ampacity in UG Duct (A) | Rated Voltage (kV)
1/0 | 0.82 | 0.88 | 80 | 1.06 | 165 | 15
2/0 | 0.87 | 0.93 | 80 | 1.1 | 190 | 15
3/0 | 0.91 | 0.97 | 80 | 1.16 | 215 | 15
4/0 | 0.96 | 1.02 | 80 | 1.21 | 245 | 15
250 | 1.01 | 1.08 | 80 | 1.27 | 270 | 15
350 | 1.11 | 1.18 | 80 | 1.37 | 330 | 15
500 | 1.22 | 1.3 | 80 | 1.49 | 400 | 15
750 | 1.4 | 1.48 | 110 | 1.73 | 490 | 15
1000 | 1.56 | 1.66 | 110 | 1.91 | 565 | 15